## EACIE
Project
Completed by |  |  |  | Date | 2020-04-05
Select Fitted / NotFit to add / remove loop driver
[9 empty] | LP 1 |  |  |  | LP 2 |  |  |  | LP 3 |  |  |  | LP 4
EACIE PANEL |  | Quiescent Load |  |  | Fire Alarm Load |  | DEVICE | DESCRIPTION | Fitted | Q | A | Weighting | Fitted | Q | A | Weighting | Fitted | Q | A | Weighting | Fitted | Q | A | Weighting |  |  | Q | A
5400 | I(A) | X | Total | I(A) | X | Total | AXIS-CWS + WSM | Axis Wall Sounder & Intelligent Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0.00315 | 0.28 | 35 | 35 | 0.00315 | 0.28 | 35 |  | OFF | 0.072 | 0.125 | 4
Chassis | 0.072 | 1 | 0.072 | 0.125 | 1 | 0.125 | AXIS-CWSV + WSM | Axis Wall Sounder VAD & Intelligent Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | DIM | 0.082 | 0.125 | 24
Sensor / Loop Current* | 0.06 | 1.25 | 0.075 | 0.06 | 1.25 | 0.075 | LVM100-ADV | Isolator Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0.00738 | 0.00738 | 0 | 82 | 0.00738 | 0.00738 | 0 |  | ON | 0.102 | 0.125 | 48
Loop Driver Loop 1 | 0.042 | 1 | 0.042 | 0.042 | 1 | 0.042 | VMC120-ADV | Relay Output Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EvacGo Logo RGB 300dpi |  |  | 72
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | VW2W100-ADV | Wireless Translator Module | 3 | 0.06 | 0.06 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MXP-503 | 0.02 | 0.02
Loop Driver Loop 2 | 0.042 | 1 | 0.042 | 0.042 | 1 | 0.042 | NONE | No Device Selected |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | MXP-509 | 0.061 | 0.061
Sensor / Loop Current* | 0.01053 | 1.25 | 0.013163 | 0.28738 | 1.25 | 0.35923 | NONE | No Device Selected |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | NONE | 0 | 0 | 5100
Loop Driver Loop 3 | 0.042 | 1 | 0.042 | 0.042 | 1 | 0.042 | [22 empty] | 5200
Sensor / Loop Current* | 0.01053 | 1.25 | 0.013163 | 0.28738 | 1.25 | 0.35923 | [19 empty] | MXP-507 | 0 | 0.03 | 5400
Loop Driver Loop 4 | 0.042 | 1 | 0.042 | 0.042 | 1 | 0.042 | [19 empty] | MXP-532 | 0.031 | 0.043
NO NETWORK Card | 0.01053 | 1 | 0.01053 | 0.28738 | 1 | 0.28738 | [19 empty] | NONE | 0 | 0
Fitted
NotFit
[26 empty] | 50 | 0.008 | 0.03
[26 empty] | 100 | 0.016 | 0.06
| 0 | 1 | 0 | 0 | 1 | 0 | [19 empty] | 150 | 0.024 | 0.09
ANCILLARY SUPPLY OUTPUT (AUX) | 0.1 | 1 | 0.1 | 0 | 1 | 0 | [19 empty] | 200 | 0.032 | 0.12
[26 empty] | 250 | 0.04 | 0.15
Sounder Output A |  |  |  | 0 | 1 | 0 | [19 empty] | F200 | 0.008 | 0.12
Sounder Output B |  |  |  | 0 | 1 | 0 | [19 empty] | NONE | 0 | 0
Sounder Output C |  |  |  | 0 | 1 | 0
Sounder Output D |  |  |  | 0 | 1 | 0
Total | ΣQuiescent Load |  | 0.45186 | ΣAlarm Load |  | 1.3738 | [21 empty] | 0.0062
Standby Duration (hours) = | 24 | Hr | 10.8445 |  | X(1.75 x 0.5) = | 1.2021 | [21 empty] | 0
|  |  |  | → (carry forward) + |  | 10.8445
[5 empty] | Total Load (Quiescent + Alarm) = | 12.0466 | [19 empty] | MXP-512 | 0.012 | 0.27
[5 empty] | X 1.25 (Battery De-rating factor)** = | 15.0583 | [19 empty] | NONE | 0 | 0
OPTIONS: | [9 empty] | 0.06 | 0.06 | 3 |  | 0 | 0 | 0 | 117 | 0.01053 | 0.28738 | 35 | 117 | 0.01053 | 0.28738 | 35 | 0
LCD DIMMING MODE | OFF | [24 empty] | MXP-504 | 0.025 | 0.034
NETWORK | NONE | [24 empty] | MXP-504/508 | 0.025 | 0.099
| NONE | [24 empty] | MXP-536 | 0.12 | 0.3
| NONE | [6 empty] | Quiescent Load | 0.06 |  |  |  | 0 |  |  |  | 0.01053 |  |  |  | 0.01053 |  |  |  |  | MXP-537 | 0.025 | 0.03
| NONE | [6 empty] | Alarm Load | 0.06 |  |  |  | 0 |  |  |  | 0.28738 | 35.0001 | 117.0017 | 0.01053 | 0.28738 | 35.0001 | 0.0017243 | 0 | 0 | MXP-547 | 0.05 | 0.05
| NONE | [6 empty] | Loop / Load Status | ok |  |  |  | ok |  |  |  | ok |  |  |  | ok |  |  |  |  | NONE | 0 | 0
MINIMUM ENCLOSURE | LARGE
REV: 02

## PSE
PSE |  | Quiescent Load |  |  | Fire Alarm Load
| I(A) | X | Total | I(A) | X | Total
Mxp-536 | 0.1 | 4 | 0.4 | 0.3 | 4 | 1.2
Mxp-537 | 0.025 | 3 | 0.075 | 0.03 | 3 | 0.09
Mxp-539 | 0.2 | 3 | 0.6 | 0.06 | 3 | 0.18
Total | ΣQuiescent Load |  | 0.4 | ΣAlarm Load |  | 1.47
Standby Duration (hours) = | 24 | Hr | 9.6 |  | X(1.75 x 0.5) = | 1.2862
|  |  |  | → (carry forward) + |  | 9.6
[5 empty] | Total Load (Quiescent + Alarm) = | 10.8863
[5 empty] | X 1.25 (Battery De-rating factor)** = | 13.6078

## Data
AXIS-CWS + WSM | Axis Wall Sounder & Intelligent Module | 9e-05 | 0.008 | 1
AXIS-CWSV + WSM | Axis Wall Sounder VAD & Intelligent Module | 9e-05 | 0.025 | 1
LVM100-ADV | Isolator Module | 9e-05 | 9e-05 | 0
NONE | No Device Selected | 0 | 0 | 0
VMC120-ADV | Relay Output Module | 0.0002 | 0.0002 | 1
VW2W100-ADV | Wireless Translator Module | 0.02 | 0.02 | 1