## AxisEN
Project
Completed by |  |  |  | Date | 2026-01-01
Take load calculated from Advanced Loop Calculator
PANEL |  | Quiescent Load |  |  | Fire Alarm Load |  |  | Q | A
5400 | I(A) | X | Total | I(A) | X | Total | OFF | 0.072 | 0.125 | 4
Chassis | 0.083 | 1 | 0.083 | 0.125 | 1 | 0.125 | DIM | 0.082 | 0.125 | 24
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | ON | 0.102 | 0.125 | 48
Loop Driver Loop 1 | 0.042 | 1 | 0.042 | 0.042 | 1 | 0.042 |  |  |  | 72
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | MXP-503 | 0.02 | 0.02
Loop Driver Loop 2 | 0.042 | 0 | 0 | 0.042 | 0 | 0 | MXP-509 | 0.043 | 0.043
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | NONE | 0 | 0 | 5100
Loop Driver Loop 3 | 0.042 | 0 | 0 | 0.042 | 0 | 0 |  |  |  | 5200
Sensor / Loop Current* | 0 | 1.25 | 0 | 0 | 1.25 | 0 | MXP-507 | 0 | 0.03 | 5400
Loop Driver Loop 4 | 0.042 | 0 | 0 | 0.042 | 0 | 0 | MXP-532 | 0.031 | 0.043
NO NETWORK Card | 0 | 1 | 0 | 0 | 1 | 0 | NONE | 0 | 0
NO PLUG-IN Card | 0 | 1 | 0 | 0 | 1 | 0
NO LED INDICATOR Card | 0 | 1 | 0 | 0 | 1 | 0
NO PRINTER | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 0.008 | 0.03
NO FAT INTERFACE | 0 | 1 | 0 | 0 | 1 | 0 | 100 | 0.016 | 0.06
| 0 | 1 | 0 | 0 | 1 | 0 | 150 | 0.024 | 0.09
ANCILLARY SUPPLY OUTPUT (AUX) | 0 | 1 | 0 | 0 | 1 | 0 | 200 | 0.032 | 0.12
[7 empty] | 250 | 0.04 | 0.15
Sounder Output A |  |  |  | 0 | 1 | 0 | NONE | 0 | 0
Sounder Output B |  |  |  | 0 | 1 | 0
Sounder Output C |  |  |  | 0 | 1 | 0 | MXP-512 | 0.012 | 0.27
Sounder Output D |  |  |  | 0 | 1 | 0 | NONE | 0 | 0
Total | ΣQuiescent Load |  | 0.125 | ΣAlarm Load |  | 0.167
Standby Duration (hours) = | 24 | Hr | 3 |  | X(2 x 0.5) = | 0.167 | MXP-504 | 0.025 | 0.034
|  |  |  | → (carry forward) + |  | 3 | MXP-504/508 | 0.025 | 0.099
[5 empty] | Total Load (Quiescent + Alarm) = | 3.167 | NONE | 0 | 0
[5 empty] | X 1.25 (Battery De-rating factor)** = | 3.9587
OPTIONS: | [6 empty] | SND 85dB | 0.0003 | 0.0035
LCD DIMMING MODE | DIM | [5 empty] | SND 90dB | 0.0003 | 0.00825
NETWORK | NONE
ROUTING / RELAY CARDS | NONE
LED CARDS - NBR OF LEDS | NONE
PRINTER | NONE
FAT/FBF/FSD/ÜE INTERFACE | NONE
MINIMUM ENCLOSURE | LARGE